## Sheet1
Event # | Event Type | Impact | Plant/Equipment | Contractual Availability Event | Start Date | End Date | Start time | End time | Description | Additional Comments | Components replaced | Status
1 | Fault | Loss of Generation | MVT 12 | Contractor Loss | 2020-07-03 | 2020-09-22 | 12:30 | 12:00 | Failed PSU 12 MVT | INV12.1 & 12.2 offline due to MVT Failure | INV12.1 & 12.2 offline due to MVT Failure | Closed
2 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2020-08-03 | 2020-08-03 | 7:30 | 20:00 | 060 Jindera - Wodonga 330kV TL | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
3 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2020-08-04 | 2020-08-04 | 8:50 | 9:20 | 060 Jindera - Wodonga 330kV TL | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
4 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2020-08-04 | 2020-08-04 | 10:45 | 13:00 | 060 Jindera - Wodonga 330kV TL | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
5 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2020-08-05 | 2020-08-05 | 9:00 | 20:00 | 060 Jindera - Wodonga 330kV TL | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
6 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2020-08-06 | 2020-08-06 | 9:00 | 20:00 | 060 Jindera - Wodonga 330kV TL | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
7 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2020-08-11 | 2020-08-11 | 7:30 | 15:00 | Dederang - Wodonga 330kV Line | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
8 | Testing | Loss of Generation | All Inverters | Contractor Loss | 2020-09-10 | 2020-09-10 | 6:00 | 16:00 | Hold point Re-test | Various Setpoint Constraints Implemented throughout day | Various Setpoint Constraints Implemented throughout day | Closed
10 | Corrective Maintenance | Loss of Generation | Inv 11.1, 11.2, 13.1, 13.2 (Feeder 6) | Contractor Loss | 2020-09-15 | 2020-09-15 | 16:30 | 17:00 | Feeder 6 isolation to allow energisation of PSU 12MVT |  |  | Closed
11 | Corrective Maintenance | Loss of Generation | Inv 11.1, 11.2, 13.1, 13.2 (Feeder 6) | Contractor Loss | 2020-09-16 | 2020-09-16 |  |  | Feeder 6 isolation to allow energisation of PSU 12MVT |  |  | Closed
12 | Corrective Maintenance | Loss of Generation | Inv 11.1, 11.2, 13.1, 13.2 (Feeder 6) | Contractor Loss | 2020-09-17 | 2020-09-17 | 11:40 | 12:00 | Feeder 6 isolation to allow energisation of PSU 12MVT |  |  | Closed
13 | Fault | Loss of Generation | All Inverters | Contractor Loss | 2020-10-21 | 2020-10-21 |  |  | 0MW generation due to PPC issue |  |  | Closed
14 | Corrective Maintenance | Loss of Generation | All Inverters | Contractor Loss | 2020-10-22 | 2020-10-22 | 14:55 | 16:15 | 0MW generation whilst works carried out to rectify the PPC |  |  | Closed
15 | Unplanned | Loss of Generation | All Inverters | Excluded Loss | 2020-10-23 | 2020-10-23 | 14:00 | 16:00 | 0MW due to incorrect bidding from RES |  |  | Closed
16 | Fault | Loss of Generation | INV 19.2 | Contractor Loss | 2020-10-30 | 2020-11-02 |  |  | Intermittent comms issues affecting generation | Rectified by SMA |  | Closed
17 | Fault | Loss of Generation | All Inverters | Contractor Loss | 2020-11-01 | 2020-11-01 | 6:15 | 11:00 | 0MW due to PPC reboot failure |  |  | Closed
18 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2020-11-03 | 2020-11-03 | 7:00 | 17:00 | 62 Wagga - Jindera 330kV TL | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
19 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2020-11-04 | 2020-11-04 | 7:00 | 17:00 | 63 Wagga - Jindera 330kV TL | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
20 | Fault | Loss of Generation | INV 3.2 | Contractor Loss | 2020-11-25 | 2020-11-25 | 9:05 | 10:11 | Inverter 3.2 Comms Error code 7620, Inverter offline. Fault reset manually. |  |  | Closed
21 | Low Performance | Loss of Generation | INV 5.1 & 5.2 | Contractor Loss | 2020-11-28 | 2020-12-08 |  |  | Intermittent Drop in performance | Ticket raised with SMA. Hard reset of both inverters & DCM Modules. Checked connection of comms cables. Inverters now performing to max output |  | Closed
22 | Fault | Comms Failure | SCADA | N/A | 2020-12-01 | 2020-12-01 | 3:00 | 7:50 | Lost remote access to SCADA system. Raised a ticket with AZZO who resolved the issue. |  |  | Closed
23 | Fault | Loss of Generation | INV 10.2 | Contractor Loss | 2020-12-01 | 2020-12-09 | 15:41 | 6:00 | INV 10.2 Offline. Identified Power stack failure. Awaiting SMA rectification | Stacks replaced on 08/12/2020 | Stacks replaced on 08/12/2020 | Closed
24 | Fault | Loss of Generation | INV 3.2 | Contractor Loss | 2020-12-04 | 2020-12-07 | 6:38 | 7:12 | INV 3.2 Offline Error code 7605 | Unsuccessful local reset performed. Ticket raised with SMA, awaiting resolution.Issue resolved remotely | Unsuccessful local reset performed. Ticket raised with SMA, awaiting resolution.Issue resolved remotely | Closed
25 | Fault | Loss of Generation | INV 3.2 | Contractor Loss | 2020-12-11 | 2020-12-11 | 7:55 | 10:20 | Error 7620 (Internal Comms error) |  |  | Closed
26 | Fault | Loss of Generation | INV 3.2 | Contractor Loss | 2020-12-15 | 2020-12-15 | 5:37 | 6:17 | Error 7620 (Internal Comms error) | Found to be loose comms patch lead. SMA to provide new patch lead. | Found to be loose comms patch lead. SMA to provide new patch lead. | Closed
27 | Fault | Loss of Generation | INV 3.2 | Contractor Loss | 2021-01-01 | 2021-01-04 | 13:01 | 8:40 | Error 7620 (Internal Comms error) | Removed, cleaned and re inserted comms patch lead. | Removed, cleaned and re inserted comms patch lead. | Closed
28 | Fault | Loss of Generation | 33kV TAMCO Switchboard | Contractor Loss | 2021-01-10 | 2021-01-30 | 18:45 | 22:55 | 33kV Incomer Panel Fault | Rectified by TAMCO | Rectified by TAMCO | Closed
29 | Fault | Loss of Generation | INV 11.2 | Contractor Loss | 2021-02-05 | 2021-02-05 | 17:23 | 17:45 | Errors 6423 | Reset remotely | Reset remotely | Closed
30 | Fault | Loss of Generation | 13.2 | Contractor Loss | 2021-02-11 | 2021-02-22 | 7:27 | 12:45 | Error 6495 - GDFI Fault | Rectified by SMA | Rectified by SMA | Closed
31 | Fault | Loss of Generation | 16.1 | Contractor Loss | 2021-02-14 | 2021-02-18 | 6:28 | 10:00 | Error 7704 - DC Switch Fault | Rectified by SMA | Rectified by SMA | Closed
32 | Fault | Loss of Generation | 17.2 | Contractor Loss | 2021-03-21 | 2021-03-22 | 8:30 | 10:01 | Ground fault on PV module strings | Rectified by isolating suspect PV module string | Rectified by isolating suspect PV module string | Closed
33 | Fault | Loss of Generation | 17.2 | Contractor Loss | 2021-03-23 | 2021-03-23 | 8:30 | 12:45 | Ground fault on PV module strings | Rectified by isolating suspect PV module string | Rectified by isolating suspect PV module string | Closed
34 | Fault | Loss of Generation | 17.2 | Contractor Loss | 2021-03-25 | 2021-03-26 | 7:30 | 15:30 | Ground fault on PV module strings | Identified broken PV module string cable | Identified broken PV module string cable | Closed
35 | Fault | Loss of Generation | PCU 10 - RMU | Contractor Loss | 2021-04-12 | 2021-04-22 | 8:15 | 18:30 | Red phase flash over fault on PCU 10 RMU SW1 | RMU Replaced | RMU Replaced | Closed
36 | Unplanned | Loss of Generation | PCU 5,6 & 9 | Contractor Loss | 2021-04-12 | 2021-04-22 | 8:15 | 18:30 | Consequential loss as a result of RMU10 SW1 Failure |  |  | Closed
37 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2021-04-21 | 2021-04-21 | 6:00 | 19:00 | Offloads 63 & 051 330kV TLs & Wagga 330 No2 TransformerX5 220kV TL de-energised | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
38 | Fault | Loss of Generation | INV 5.2 | Contractor Loss | 2021-04-22 | 2021-04-29 | 18:30 | 12:30 | Failed Comms Card | Comms Card replaced by SMA | Comms Card replaced by SMA | Closed
39 | Fault | Loss of Generation | INV 3.2 | Contractor Loss | 2021-06-04 | 2021-06-23 | 12:15 | 8:00 | Inverter fault - Unspecified error code | Ticket raised with SMA. SMA visited site, however, will require tech support form Germany.Single stack replaced which resolved the issue | Ticket raised with SMA. SMA visited site, however, will require tech support form Germany.Single stack replaced which resolved the issue | Closed
40 | Fault | Loss of Generation | MCP UPS (affecting all inverters) | Contractor Loss | 2021-06-06 | 2021-06-06 | 2:06 | 11:15 | UPS fault causing loss off comms consequently 0 generation of all inverters | Replaced UPS | Replaced UPS | Closed
41 | Fault | Loss of Generation | INV 13.2 | Contractor Loss | 2021-06-06 | 2021-06-09 | 11:15 | 14:30 | GDFI issue - Inverter offline | SMA resolved on site, replaced GFDI CB | SMA resolved on site, replaced GFDI CB | Closed
42 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2021-06-11 | 2021-06-11 | 7:00 | 21:30 | TG outage, constraint to 0MW | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
43 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2021-06-15 | 2021-06-15 | 6:30 | 16:30 | TG outage, constraint to 0MW | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
44 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2021-06-16 | 2021-06-16 | 6:20 | 14:30 | TG outage, constraint to 0MW | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
45 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2021-06-17 | 2021-06-17 | 7:00 | 17:30 | TG outage, constraint to 0MW | Constrained to 0MW and all inverters disconnected | Constrained to 0MW and all inverters disconnected | Closed
46 | Corrective Maintenance | Loss of Generation | INV 17.2 | Contractor Loss | 2021-07-14 | 2021-07-14 | 12:00 | 13:00 | Identified faulty DST 2board | Replaced board. SMA ticket #405977644 | Replaced board. SMA ticket #405977644 | Closed
47 | AEMO/TransGrid Constraint | Loss of Generation | 132kV incomer isolated | Excluded Loss | 2021-07-23 | 2021-07-23 | 7:00 | 18:00 | Work to repair Inoperable 9J5 Bus Disconnector at Wagga North. Subsequently will result in 0MW generation from Bomen Solar Farmfor the duration of outage. | TG outage, constraint to 0MW | TG outage, constraint to 0MW | Closed
48 | Fault | Loss of Generation | INV 7.1 | Contractor Loss | 2021-07-24 | 2021-07-24 | 12:00 | 17:00 | Low insulation resistance fault | Operator intervention and was back online by 5pm | Operator intervention and was back online by 5pm | Closed
49 | Fault | Loss of Generation | INV 7.1 | Contractor Loss | 2021-07-31 | 2021-07-31 | 8:00 | 11:00 | Low insulation resistance fault | Identified faulty MC4 plug |  | Closed
50 | Fault | Loss of Generation | INV 7.1 | Contractor Loss | 2021-08-16 | 2021-08-16 | 9:27 | 10:30 | Low insulation resistance fault | Reset remotely |  | Closed
51 | Fault | Loss of Generation | INV 18.1 & 18.2 | Contractor Loss | 2021-08-04 | 2021-08-18 | 7:00 | 12:30 | Suspected Temp Limp Mode , derates / reduces output | Ticket raised with SMA (406009111). Tim successfully changed G1 Power Supply in station 18 and both inverters are operating to full potential.Replacement G1 Power Supply ordered by SMA |  | Closed
52 | Fault | Loss of Generation | INV 7.1 | Contractor Loss | 2021-09-04 | 2021-09-06 | 12:55 | 9:35 | Low insulation resistance fault | Identified damaged string cable. | UG string cable replaced by Beon | Closed
53 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2021-09-16 | 2021-09-18 | 18:30 | 21:30 | TG outage, constraint to 0MW | Constrained to 0MW and all inverters disconnected |  | Closed
54 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2021-09-20 | 2021-09-20 | 6:30 | 18:30 | TG outage, constraint to 0MW | Constrained to 0MW and all inverters disconnected |  | Closed
55 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2021-11-01 | 2021-11-06 | 5:00 | 10:00 | TG outage, constraint to 0MW | Constrained to 0MW and all inverters disconnected |  | Closed
56 | Planned | Loss of Generation | All Inverters | Contractor Loss | 2021-11-17 | 2021-11-17 | 11:00 | 13:00 |  | Droop voltage setting change including testing |  | Closed
57 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2021-11-27 | 2021-11-29 | 6:30 | 21:00 | TG outage, constraint to 0MW | Constrained to 0MW and all inverters disconnected |  | Closed
58 | Low Performance | Loss of Generation | INV 2.2 | Contractor Loss | 2021-11-30 | 2021-12-01 | 6:30 | 14:30 | SMA firmware error | SMA re applied firmware |  | Closed
59 | Fault | Loss of Generation | INV 21.1 | Contractor Loss | 2021-12-13 | 2021-12-13 | 6:00 | 11:00 | Start up fault/low insulation resistance fault under investigation |  |  | Closed
60 | Fault | Loss of Generation | INV 21.1 | Contractor Loss | 2021-12-15 | 2021-12-15 | 7:00 | 11:00 | Start up fault/low insulation resistance fault under investigation |  |  | Closed
61 | Fault | Loss of Generation | INV 21.1 | Contractor Loss | 2021-12-16 | 2021-12-16 | 6:00 | 8:30 | Low insulation resistance fault found to be a burnt MC4 plug | Plug and cable to be replaced | MC4 plug and cable replaced by Beon | Closed
62 | Fault | Loss of Generation | INV 16.1 | Contractor Loss | 2021-12-28 | 2021-12-28 | 5:30 | 6:30 | Low insulation resistance fault under investigation | Identified damaged string cable. |  | Closed
63 | Fault | Loss of Generation | INV 16.1 | Contractor Loss | 2021-12-29 | 2021-12-29 | 6:20 | 9:00 | Low insulation resistance fault under investigation | Identified damaged string cable. |  | Closed
64 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2022-01-06 | 2022-01-06 | 5:00 | 7:30 |  | TG outage, constraint to 0MW |  | Closed
65 | Planned |  |  | Contractor Loss | 2022-02-17 | 2022-02-17 | 8:00 | 12:30 | Ramp rate remediation testing with TG/AEMO | Works to remediate ramp rate NCR |  | Closed
66 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2022-02-18 | 2022-02-19 | 20:00 | 15:00 |  | TG outage, constraint to 0MW |  | Closed
67 | Fault | Loss of Generation | 1.1, 1.2, 7.1, 7.2, 8.1, 8.2, 14.1, 14.2, 4.2 | Contractor Loss | 2022-03-10 | 2022-03-10 | 7:30 | 14:30 | Root cause of event to be determined | Inverters required powercycle reset |  | Closed
68 | Fault | Loss of Generation | Various inverters | Contractor Loss | 2022-03-11 | 2022-03-11 | 7:00 | 10:00 |  | Inveretrs requiring powercycle reset |  | Closed
69 | Fault | Loss of Generation | PCU 19,20,21 & 22 | Contractor Loss | 2022-03-12 | 2022-03-12 | 7:00 | 8:30 |  | Inveretrs requiring powercycle reset |  | Closed
70 | Fault | Loss of Generation | INV 18.1 | Contractor Loss | 2022-03-15 | 2022-03-15 | 7:40 | 13:30 | Inverter fault - Ticket raised with SMA | Faulty DST board replaced . DST board will be replenish by SMA under warranty | Faulty DST board replaced - SMA | Closed
71 | Testing | Loss of Generation | All Inverters | Contractor Loss | 2022-04-05 | 2022-04-05 | 9:45 | 11:45 | R2 Model Validation Testing - Frequency Raise and Lower Test |  |  | Closed
72 | Planned Maintenance | Loss of Generation | Collector Station and all PCU's | Excluded Loss | 2022-04-19 | 2022-04-20 | 14:30 | 19:00 | Annual HV maintenance at Collector station and all PCU's |  |  | Closed
73 | Planned Maintenance | Loss of Generation | Inverter | Contractor Loss | 2022-05-02 | 2022-05-26 |  |  | Annual Maintenance conducted on the inverters. Multiple times/days as per schedule provided. |  |  | Closed
74 | Fault | Loss of Generation | Inverter 16.1 | Contractor Loss | 2022-07-09 | 2022-07-17 |  |  | UG cable fault under investigation with SMA. Multiple intermittent times. Underground string cable to be replaced. |  |  | Open
75 | Corrective Maintenance | Loss of Generation | INV 12.1, 12.2, 11.1, 11.2 | Contractor Loss | 2022-07-25 | 2022-07-27 | 13:00 | 14:00 | Replace MVT 12 |  |  | Closed
76 | Corrective Maintenance | Loss of Generation | INV 12.1, 12.2 | Contractor Loss | 2022-07-27 | 2022-07-28 | 14:00 | 7:30 | MVT12 soak prior to on load |  |  | Closed
77 | Corrective Maintenance | Comms Failure | INV 12.1 | Contractor Loss | 2022-08-01 | 2022-08-11 |  |  | NCU 24 intermittent faults. Replaced under warranty |  | NCU replaced - Nextracker | Closed
78 | Fault | Loss of Generation | PCU 18 | Contractor Loss | 2022-08-18 | 2022-08-23 |  |  | Earth fault, Intermittent issues. Faulty MVT fan control relay replaced under warranty |  | MVT fan replaced - SMA | Closed
79 | Fault | Comms Failure | Multiple inverters | Contractor Loss | 2022-09-06 | 2022-09-21 |  |  | Multiple Inverters Comms fault. Inverters power cycled and returned to normal operations |  |  | Closed
80 | Fault | Loss of Generation | INV 5.1 | Contractor Loss | 2022-10-02 | 2022-10-02 | 9:02 | 12:00 | IR failure. Fault isolated and inverter returned to service |  | Fuse holder replaced - Beon | Closed
79 | AEMO/TransGrid Constraint | Loss of Generation | All Inverters | Excluded Loss | 2022-10-25 | 2022-10-26 | 5:00 | 23:00 | TG outage, constraint to 0MW |  |  | Closed
80 | Fault | Loss of Generation | Inverter 17.1 | Contractor Loss | 2022-11-21 | 2022-11-21 | 6:45 | 7:30 | Earth fault | Underground string cable to be replaced SCB 17-1-7 Row 8 (Mech No Row 17-2-81) |  | Open
81 | Fault | Loss of Generation | Inverter 17.1 | Contractor Loss | 2022-11-21 | 2022-11-21 | 8:54 | 10:25 | Earth fault | Underground string cable to be replaced SCB 17-1-7 Row 8 (Mech No Row 17-2-81) |  | Open
82 | Fault | Comms Failure | Inverter 11.1 | Contractor Loss | 2022-12-01 | 2022-12-01 |  | 7:30 | Communication Fault | Inverter requiring powercycle reset | Nil | Closed
83 | Fault | Comms Failure | Inverter 11.2 | Contractor Loss | 2022-12-01 | 2022-12-01 |  | 7:45 | Communication Fault | Inverter requiring powercycle reset | Nil | Closed
84 | Fault | Comms Failure | Inverter 12.1 | Contractor Loss | 2022-12-01 | 2022-12-01 |  | 7:50 | Communication Fault | Inverter requiring powercycle reset | Nil | Closed
85 | Fault | Comms Failure | Inverter 12.2 | Contractor Loss | 2022-12-01 | 2022-12-01 |  | 8:40 | Communication Fault | Inverter requiring powercycle reset | Nil | Closed
86 | Fault | Comms Failure | Inverter 13.1 | Contractor Loss | 2022-12-01 | 2022-12-01 |  | 8:05 | Communication Fault | Inverter requiring powercycle reset | Nil | Closed
87 | Fault | Comms Failure | Inverter 13.2 | Contractor Loss | 2022-12-01 | 2022-12-01 |  | 8:00 | Communication Fault | Inverter requiring powercycle reset | Nil | Closed
88 | Fault | Loss of Generation | Inverter 17.1 | Contractor Loss | 2022-12-02 | 2022-12-02 |  | 7:25 | Earth Fault | Underground string cable to be replaced SCB 17-1-7 Row 6 | Nil | Closed
89 | Fault | Loss of Generation | Inverter 16.1 | Contractor Loss | 2022-12-16 | 2022-12-17 | 21:35 | 11:30 | Communication Fault | Inverter requiring powercycle reset | Nil | Closed
90 | Unplanned | Loss of Generation | Inverter 16.2 | Contractor Loss | 2022-12-16 | 2022-12-17 | 21:35 | 11:30 | Derating due to 16.1 comms fail | Inverter requiring powercycle reset | Nil | Closed
91 | Fault | Loss of Generation | Inverter 12.2 | Contractor Loss | 2023-01-05 | 2023-01-05 | 6:00 | 7:40 | Earth Fault | Underground string cable to be replaced SCB 12.2.8 Strings 5,6 & 8 | Nil | Open
92 | Fault | Comms Failure | Inverter 21.1 | Contractor Loss | 2023-01-11 | 2023-01-11 | 6:15 | 7:35 | Communication Fault | Loss weather station 1 &2 as well | Nil | Closed
93 | Fault | Comms Failure | Inverter 21.2 | Contractor Loss | 2023-01-11 | 2023-01-11 | 6:15 | 7:45 | Communication Fault | Loss weather station 1 &2 as well | Nil | Closed
94 | Fault | Comms Failure | Inverter 22.1 | Contractor Loss | 2023-01-11 | 2023-01-11 | 6:15 | 7:55 | Communication Fault | Loss weather station 1 &2 as well | Nil | Closed
95 | Fault | Comms Failure | Inverter 22.2 | Contractor Loss | 2023-01-11 | 2023-01-11 | 6:15 | 7:55 | Communication Fault | Loss weather station 1 &2 as well | Nil | Closed
96 | Fault | Comms Failure | Inverter 19.1 | Contractor Loss | 2023-01-11 | 2023-01-11 | 18:35 | 18:50 | Communication Fault | Inverters required powercycle reset | Nil | Closed
97 | Fault | Comms Failure | Inverter 19.2 | Contractor Loss | 2023-01-11 | 2023-01-11 | 17:55 | 18:55 | Communication Fault | Inverters required powercycle reset | Nil | Closed
98 | Fault | Comms Failure | Inverter 20.1 | Contractor Loss | 2023-01-11 | 2023-01-11 | 17:40 | 19:10 | Communication Fault | Inverters required powercycle reset | Nil | Closed
99 | Fault | Comms Failure | Inverter 20.2 | Contractor Loss | 2023-01-11 | 2023-01-11 | 18:05 | 19:20 | Communication Fault | Inverters required powercycle reset | Nil | Closed
100 | Fault | Comms Failure | Inverter 14.1 | Contractor Loss | 2023-01-14 | 2023-01-14 | 15:50 | 20:20 | Communication Fault | Inverters required powercycle reset | Nil | Closed
101 | Fault | Comms Failure | Inverter 15.1 | Contractor Loss | 2023-01-14 | 2023-01-14 | 19:05 | 20:20 | Communication Fault | Inverters required powercycle reset | Nil | Closed
102 | Fault | Comms Failure | Inverter 15.2 | Contractor Loss | 2023-01-14 | 2023-01-14 | 18:25 | 20:20 | Communication Fault | Inverters required powercycle reset | Nil | Closed
103 | Fault | Comms Failure | Inverter 16.2 | Contractor Loss | 2023-01-14 | 2023-01-14 | 19:25 | 20:20 | Communication Fault | Inverters required powercycle reset | Nil | Closed
104 | Fault | Comms Failure | Inverter 14.2 | Contractor Loss | 2023-01-15 | 2023-01-15 | 7:10 | 7:30 | Communication Fault | Inverters required powercycle reset | Nil | Closed
105 | Fault | Loss of Generation | PCU 10 INV 1 & 2 | Contractor Loss | 2023-01-18 | 2023-01-19 | 19:37 | 10:19 | CB trip on INV 10.1. | Identified capacitor failure. SMA case raised #406527901. |  | Closed
106 | Fault | Loss of Generation | PCU 10 INV 1 | Excluded Loss | 2023-01-19 | 2023-02-16 | 10:19 | 13:05 | Awaiting SMA parts and repairs to be carried out. | Identified capacitor failure. SMA case raised #406527901. | Main fan, Cont Board , Comms Board | Closed
107 | Fault | Loss of Generation | PCU 2 INV 2 | Contractor Loss | 2023-01-24 | 2023-01-24 | 7:45 | 8:10 | Communication Fault | Inverters required powercycle reset | Nil | Closed
108 | Fault | Loss of Generation | PCU 4 INV 2 | Contractor Loss | 2023-01-24 | 2023-01-24 | 9:05 | 9:40 | Communication Fault | Inverters required powercycle reset | Nil | Closed
109 | Fault | Loss of Generation | PCU 6 INV 1 | Contractor Loss | 2023-01-25 | 2023-01-25 | 6:45 | 7:50 | Communication Fault | Inverters required powercycle reset | Nil | Closed
110 | Fault | Loss of Generation | PCU 6 INV 2 | Contractor Loss | 2023-01-25 | 2023-01-25 | 6:45 | 7:40 | Communication Fault | Inverters required powercycle reset | Nil | Closed
111 | Fault | Loss of Generation | PCU 5 INV 1 | Contractor Loss | 2023-01-25 | 2023-01-25 | 11:15 | 11:40 | Communication Fault | Inverters required powercycle reset | Nil | Closed
112 | Fault | Loss of Generation | PCU 5 INV 1 | Contractor Loss | 2023-02-06 | 2023-02-06 | 6:25 | 8:25 | Communication Fault | Inverters required powercycle reset | Nil | Closed
113 | Fault | Loss of Generation | PCU 5 INV 2 | Contractor Loss | 2023-02-15 | 2023-02-16 | 10:45 | 10:45 | Buffer power supply fault | required SMA investigation | Nil | Closed
114 | Planned Maintenance | Loss of Generation | PCU 1 INV 1.2 | Excluded Loss | 2023-03-08 | 2023-03-08 | 11:00 | 12:30 | Stack 2 DST board replacement | SMA investigation and action | Driver Board SC30DST.BG4 Kit | Closed
115 | Fault | Loss of Generation | PCU18 INV 18.1 | Contractor Loss | 2023-03-30 | 2023-03-30 | 13:05 | 13:25 | DC system Ground fault | Underground string failure | Nil | Open
116 | Fault | Loss of Generation | PCU18 INV 18.1 | Contractor Loss | 2023-03-31 | 2023-03-31 | 9:15 | 9:40 | DC system Ground fault | Underground string failure | Nil | Open
117 | Fault | Loss of Generation | PCU18 INV 18.1 | Contractor Loss | 2023-03-31 | 2023-03-31 | 12:00 | 13:50 | DC system Ground fault | Underground string failure | Nil | Open
118 | Fault | Loss of Generation | PCU18 INV 18.1 | Contractor Loss | 2023-04-04 | 2023-04-04 | 13:25 | 14:20 | DC system Ground fault | Underground string failure | Nil | Open
119 | Fault | Loss of Generation | PCU18 INV 18.1 | Contractor Loss | 2023-04-05 | 2023-04-06 | 11:50 | 12:55 | DC system Ground fault | Underground string failure | Nil | Open
120 | Fault | Loss of Generation | PCU22 INV 22.1 | Contractor Loss | 2023-04-08 | 2023-04-27 | 13:15 | 12:50 | Capacitor Bank Failure | SMA investigation and action | All spare parts replaced by SMA | Closed
121 | Fault | Comms Failure | PCU16 INV 16.1 | Contractor Loss | 2023-04-23 | 2023-04-23 | 6:30 | 11:55 | SCADA alarm - No time sync informatiom | SMA Alarm Code 8713 - time out in comms - for grid mgmt- device switching off | Nil | Closed